## Slide 1: I/O DEVICES FOR PROCESS CONTROL AND INSTRUMENTATION
Definition :
An instrument or a process control system comprises a number of components which together perform measurement or control one or more physical parameters.
Examples of physical parameters are temperature, pressure etc.
1

## Slide 2
Functionally, the three operations are performed:
Monitoring of one or more physical parameters or process control variables and acquisition of relevant data.
Processing of the acquired data.
Controlling of physical parameters by generating suitable control signals.
2

## Slide 3
Three major elements of process control system are :
      Input devices
      Processing device
      Output devices
The function of the processing device is to be performed by an MPU and necessary input and output devices are to be interfaced to it.
3

## Slide 4
System Bus
MICROCOMPUTER
IO PORTS
IO PORTS
IO PORTS
IO PORTS
ADCS
Opto couplers
DAC
Relays
transducers
INDUSTRIAL PROCESS
Figure : Basic block diagram of process control system.
4

## Slide 5: TRANSDUCER
Definition:
Transducer is a special device which converts non-electrical entities to electrical signals.
Classification:
i) Active
ii) Passive
5

## Slide 6
Active Transducer
Generates electrical signal in response to the physical parameters and does not require any electrical energy.
Example
    Piezo electric sensor
    Thermo electric devices
    Photo Voltaic Cell
Passive Transducer
Requires external energy for its operation.
  Example
    Piezo-resistive sensors
    Thermo-resistive sensor
    Photo Conductive devices
6

## Slide 7
Properties of Transducer:
a) Linearity
b) Sensitivity
c) Dynamic range
d) Repeatability
e) Physical size
7

## Slide 8
Linearity
A linear relationship between the physical parameter value and the value of the equivalent electrical quantity is preferable.
Sensitivity
A higher change in the value of the electrical quantity per unit change of the physical parameter will provide better accuracy for measurement.
Dynamic range
The range of physical parameter over which the transducer operates.
Repeatability
The behavior of the transducer should not change with ageing.
Physical size
The size should be small, so that the presence of the transducers does not disturb the prevalent environment of the system.
8

## Slide 9: Different classes of transducer
Temperature transducer
    Resistive thermometers
    Thermistor
    Thermocouple
    IC Temperature Sensors (Home Work)
9

## Slide 10: Resistance thermometers:
Thin (0.05 mm diameter) wire of temperature sensitive metal is wound on a suitable supported inside a tiny Pyrex tube.
It is then placed in the environment for which the temperature has to be measured.
Temperature are measured in this way-
Rt = R0(1+α(Tt-T0))
R0=is the resistance at temperature T0
Rt=is the resistance at temperature Tt
α=is the temperature coefficient used for making the wire
10

## Slide 11
Example: A platinum resistance thermometer uses the change in R to measure temperature. Suppose R0 = 50 Ω at T0=20 ºC.
α for Pt is 3.92×10-3 (ºC)-1 in this temperature range. What is R when T = 50.0 ºC?
Answer:
R = 50Ω [1 + 3.92 ×10-3 (ºC)-1 (30.0 ºC)] = 55.9 Ω
Rt = R0(1+α(Tt-T0))

## Slide 12
Example: A platinum resistance thermometer has a resistance R0 = 50.0 Ω at T0=20 ºC. α for Pt is 3.92×10-3 (ºC)-1. The thermometer is immersed in a vessel containing melting tin, at which point R increases to 91.6Ω. What is the melting point of tin?
Answer:
R=R0 [1+ α(T - T0 )]
91.6Ω = 50Ω [1 + 3.92 ×10-3 (T–20ºC)]
1.83 = [1 + 3.92 ×10-3 (T–20ºC)]
0.83 = 3.92 ×10-3 (T–20ºC)
212ºC = T–20ºC
T = 232 ºC

## Slide 13: Thermistors:
Thermistor is a semiconductor material
fabricated from sintered mixture of metal alloys is
widely used because-
    Compactness.
    High sensitivity.
    High resistivity.
The relation between the resistance and temperature is-
Rt=R0 exp [β (1/Tt-1/T0)]
R0=is the resistance at temperature T0
Rt=is the resistance at temperature Tt
β=is the characteristics coefficient of the thermistor material. It is negative and nonlinear.
13

## Slide 14: Thermocouple:
A thermocouple is an active temperature transducer for wide range (0-2500^c).
It consists of 2 junction (j1 & j2) of 2 different metal(A & B) in the figure.
A
T1
T2
A
j1
j2
Fig: schematic diagram of a thermocouple
14

## Slide 15: Thermocouple
An emf is developed between the terminals T1 and T2 if there is a temperature difference between the junctions J1 and J2.
The magnitude of the emf depends on the two metals and the temperature difference between the two junctions.
15

## Slide 16: Temperature Transducer
Resistance Temperature Detectors (RTDs)
  Platinum, Nickel, Copper metals are typically used
  positive temperature coefficients
Thermistors (“thermally sensitive resistor”)
  formed from semiconductor materials, not metals
    often composite of a ceramic and a metallic oxide (Mn, Co, Cu or Fe)
  typically have negative temperature coefficients
Thermocouples
  based on the Seebeck effect: dissimilar metals at diff. temps. 🡪 signal
16

## Slide 17: Reference:
Microprocessor :Principles and Applications
-By Ajit Pal
Chapter 7
17